## Battery calculation
Fire alarm battery calculation — NFPA 72 2019 / 2022
Required Ah = (standby current × standby hours + alarm current × alarm hours) × factor. Factor: 2019 10.6.7.2.1.1 «minimum 20 percent safety margin» = 1.2 · 2022 10.6.7.2.14 «minimum correction factor of 1.25 for aging» = 1.25. Free from strobeline.com/fire-alarm-battery-calculation · not an official NFPA form.
Property
NFPA 72 edition | 2022
Standby hours | 24 | 24 h for protected premises (10.6.7.2.1) — longer if the AHJ or the design asks
Alarm time (minutes) | 5 | Alarm minutes by system: Fire alarm 5 · In-building voice evacuation (EVACS) 15 · In-building mass notification 15 · Carbon monoxide detection, monitored by a supervising station 5 · Carbon monoxide detection, not monitored 720 · Two-way emergency communications 240
Factor
Enter each load: quantity and current per unit in amps (mA ÷ 1000). Totals and the required capacity below update by themselves.
Device or load | Quantity | Standby A per unit | Alarm A per unit | Standby A total | Alarm A total
Totals
Standby Ah
Alarm Ah
Subtotal Ah
Required battery capacity (Ah) |  | Pick a battery at or above this rating.